Specification

Product:		Dust Collector

Application:		The Mini-Vac is designed for direct source capture of pollutants through one or

two 3” flexible, self-supported pickup hoses.

Revision:		March 30, 2009

1.	Mini-Vac (www.LEV-CO.com)

1.1.	General:

1.1.1.	The following direct drive fans shall be of industrial quality, and be designed to be used for direct source capture of pollutants through one or two 3” flexible, self-supported pickup hoses. They shall be manufactured to withstand the environments associated with these applications and shall remove the pollutants in accordance with all industrial ventilation guidelines.

1.2.	Construction:

1.2.1.	Mini-Vac collects dust, welding smoke, and other dry pollutants in industrial plants, shops, schools and factories.

1.2.2.	The Mini-Vac is designed for direct source capture of pollutants through one or two 3” flexible, self-supported pickup hoses.

1.2.3.	Filtration – first stage: Dirty air enters the unit through the top or side and enters the first stage 2” pleated filter that removes large particles.

1.2.4	Second stage is a 6” deep, extended surface cartridge filter rated at 95% efficiency.

1.2.5.	Third stage is a 1” charcoal filter for gas/odor control.

1.2.6.	Air then exits through the motor/blower, into the built-in silencer, and then out through the bottom grille. 1.2.7.	Cartridge life ranges from several months to a year or more depending on the application and quantity of pollutants collected.

1.2.8.	Pressure gauge indicates when filters are dirty.

1.2.9.	Optionally, the compartment may be lined with 1/2” acoustic material for maximum noise reduction.

1.2.10.	The model Mini-Vac is a complete portable collector.

1.2.11.	The unit comes equipped with four, 2" swivel casters and a hinged front access door to filters. It is available with a single, 3” diameter, 3-1/2’* long, self-supported pickup arm mounted directly on the unit, or it can be ordered with a side inlet and remote plenum that can be bolted to a work bench which includes a 3” diameter, 3-1/2’ long, self-supported hose, and 5’ of connecting hose.

1.2.12.	Dual options of the above are also available.

1.2.13.	Other options include 5’ long arm(s) in place of 3-1/2’ long arm(s), or a 4” diameter, 5’ long arm in place of the standard 3” diameter arm(s).

1.2.14.	The Mini-Vac is also available with (2) 3” inlets on the side and no arms.

1.2.15.	18 gauge steel cabinet finished with a two part chemical and oil resistant paint.

    - Includes Ultra-SealTM Filter mounting system, hinged front access door to filters, (4) 2” swivel casters, filter change indicator gauge,

1.3.	 Specification:

1.3.1.	STD DIM: 13.25" W x 20.50” D x 27.38" H [0.34m W x 0.52m D x 0.70m H]

1.3.2.	WEIGHT: 83 lb. [38 kg]

1.3.3.	Fully enclosed motor/blower, on-off switch, and 6’ power cord.

1.3.4.	NOISE LEVEL: 61 dBA

1.3.5	ELECTRICAL:

Standard Motor/Blower: 1/2 HP 115V, 1 phase, 60 Hz @ 7.4 A

Optional Motor/Blower: 1/2 HP 220V, 1 phase, 50 Hz @ 2.8 A (50 Hz operation only)

1.3.6.	FILTRATION:

STANDARD OPTIONS

1st Stage: 2” pleat N/A

2nd Stage: 95% ext. surface cartridge* 99.97% HEPA AD Module

3rd Stage: 1” charcoal 1” poly after-filter

1.3.7.	Flow rate:

- one arm 	125 CFM

- two arms	200 CFM

- three arms	300 CFM

1.4	Options:

1.4.1	Internal HEPA filter

1.4.2	Absorption module

1.5.	Performance ratings

1.5.1	See spec drawing for performance curves